| EDMS No. 3460560 | EP/ATLAS |
| --- | --- |
| Price Enquiry Technical Specification Supply of Ventilation Chassis for 19” Racks |  |

Abstract

This Technical Specification concerns the supply of 50 units of Ventilation Chassis for 19’’ Racks.

The delivery is foreseen 16 weeks from the notification of the Contract.

Table of Contents

1.	INTRODUCTION	1

1.1	Introduction to CERN	1

1.2	Introduction to the ATLAS facility	2

2.	SCOPE OF THE SUPPLY	2

2.1	General Description	2

2.2	Content of the Supply	2

3.	SPECIFICATION OF THE TECHNICAL DELIVERABLES	3

3.1	Materials and Components	3

3.2	Characteristics and Performances	3

3.3	Operational and Environmental Conditions	5

4.	SPECIFICATION OF THE ACTIVITIES	5

4.1	Activities at the Contractor’s Premises	5

5.	SPECIFICATION OF THE DOCUMENTATION	6

5.1	Documentation Related to the Supply	6

6.	APPLICABLE RULES, NORMS AND STANDARDS	6

6.1	Norms and Standards	6

7.	PERFORMANCE OF THE CONTRACT	7

7.1	Schedule	7

7.2	Contract Follow-Up and Progress Monitoring	7

7.3	Acceptance of the Supply by CERN	7

8.	CERN REPRESENTATIVES	8

9.	ANNEXES	8

Table of Acronyms

| Acronym | Definition |
| --- | --- |
| ATLAS | A Toroidal LHC ApparatuS |
| EU | European Union |
| LHC | Large Hadron Collider |
| IEC | International Electrotechnical Commission |
| ISO | International Organization for Standardization |

# INTRODUCTION

The Contract will be performed in accordance with the General Conditions of CERN Contracts (CERN/FC/6674-II). However, this Technical Specification prevails over the General Conditions of CERN Contracts with regard to the particular provisions specified in this document, and this without prejudice to any other provision in the General Conditions of CERN Contracts.

Capitalised terms in the body text are defined either in the General Conditions of CERN Contracts or in the present document.

## Introduction to CERN

CERN, the European Organization for Nuclear Research, is an intergovernmental organization with over 30 Member States1. Its seat is in Geneva, but its premises are located on both sides of the French- Swiss border (https://maps.web.cern.ch/). CERN’s mission is to enable international collaboration in the field of high-energy particle physics research and to this end it designs, builds, and operates particle accelerators and the associated experimental areas. At present, more than 10 000 scientific users from research institutes all over the world are using CERN’s installations for their experiments. Further information is available on the CERN website: http://cern.ch.

The accelerator complex at CERN is a succession of machines with increasingly higher energies. Each machine injects the beam into the next one, which takes over to bring the beam to an even higher energy, and so on. The flagship of this complex is the Large Hadron Collider (LHC) (see Figure 1).

Figure 1: CERN Accelerator Complex

1 http://home.web.cern.ch/about/member-states

## Introduction to the ATLAS facility

ATLAS, or A Toroidal LHC ApparatuS (https://atlas.cern ), is a particle physics experiment at the Large Hadron Collider (LHC) at CERN. The ATLAS detector is designed and constructed to make new particle discoveries resulting from head-on collisions of protons produced by the LHC of extraordinarily high energy. ATLAS will investigate the basic forces that have shaped our Universe since the beginning of time and that will determine its fate. Among the possible discovery candidates are particles that could explain the origin of mass, confirm the existence of extra dimensions in space, unification of fundamental forces, and evidence of dark matter in our Universe. The ATLAS detector is located in an underground cavern on the Swiss part of the CERN site. The experiment is in operation and produces physics results. The ATLAS collaboration involves more than 3000 scientists from 174 institutions in 38 countries.

# SCOPE OF THE SUPPLY

CERN intends to place a contract (the “Contract”) for the supply of Ventilation Chassis for 19’’ Racks (the “Chassis(s)”, and in whole or in part, the “Supply”).

The successful Bidder (the “Contractor”) shall provide the Supply as defined in this Technical Specification, including its annexes.

## General Description

The Supply consists in the supply of 50 units of Ventilation Chassis for 19’’ Racks. The chassis is intended for integration into a standard 19-inch rack, and it is used in a ventilation application.

The chassis is a mechanically assembled structure composed of multiple laser-cut and bent metallic components. It is designed to provide structural support, ensure proper positioning within the rack, and allow unobstructed airflow through the system. The assembly includes all necessary structural elements, mounting interfaces, and fastening provisions required for installation.

The design is based on an existing configuration and shall be reproduced accordingly, ensuring compatibility with the current rack infrastructure. The chassis shall be manufactured in accordance with the provided CAD model (see Annex A) and technical requirements, ensuring consistency with the original design in terms of geometry, assembly, and functional performance.

The supply includes all components required to deliver a complete and ready-to-install chassis assembly, including metallic parts, integrated threaded elements or inserts where applicable, and any non-metallic components present in the design.

## Content of the Supply

The Supply shall include:

- Technical deliverables as specified in § 3:

  - One prototype unit;

  - 49 series units of Ventilation Chassis for 19’’ Racks;

- Activities as specified in § 4, on the Contractor site:

  - Prototyping (see § 4.1.2);

  - Series Manufacturing (see § 4.1.3);

  - Packing and Shipping if requested (see § 4.1.4).

- Documentation as specified in § 5:

  - Documentation Related to the Supply (see § 5.1);

# SPECIFICATION OF THE TECHNICAL DELIVERABLES

The Supply shall include the technical deliverables as specified in the present section. In the framework of this procurement, the production of a prototype and series units is required.

## Materials and Components

The Supply (except part no:19) shall be made out of non-magnetic metal, either aluminium or stainless-steel. In order to ensure protection against corrosion, the panels shall undergo a passivation treatment (Alodine 1200 or similar).

## Characteristics and Performances

The Racks shall comply with the following characteristics and performance requirements:

The components of the Chassis shall be rigid enough to support the assembly of the two tangential fans, of the electrical motors as well as magnetic shielding and the effects of magnetic fields. Subcomponents (e.g. fans, motors, shielding) are not part of the supply. See Annex C for information purposes, § 9. Annexes.

The handles (see Annex A, Part no: 18, § 9. Annexes.) shall be firmly fixed to the frame in order to support the weight of the Chassis and its equipment (approximately 35kg).

Table 1: Design & Construction

| DESIGN & CONSTRUCTION |  |
| --- | --- |
| Design | The chassis shall be manufactured in accordance with the provided CAD model and shall comply with IEC 60297-3 for a 4U high sub-rack. See Annex A, § 9. Annexes. |
| Material | - Metallic parts: Either aluminium or stainless-steel, the panels shall undergo a passivation treatment (Alodine 1200 or similar). - Plastic parts (Part no: 19 , there are only 2 small plastic rails for mon card) Material certificates in accordance with EN 10204 shall be provided (minimum type 2.2). |
| General Tolerances | - General: ISO 2768-mK - Holes: ± 0.1 mm - Centre-to-centre distances (e.g. hole spacing): ± 0.2 mm Unless otherwise specified, the above tolerances apply. For critical dimensions, individually specified tolerances shall prevail. |
| Critical Dimensions | - Inner height (distance between upper and lower damper support rails, Part no: 37): 165 +0.3 / 0 mm - Alignment pins position (Part no: 15): See Annex B, § 9. Annexes. - Rail seat width (bottom support surface, Part no: 37): 18 +0.5 / 0 mm Rail internal clear width (between inner vertical faces, Part no: 37): 19 +0.5 / 0 mm See Annex B, § 9. Annexes. |
| Fastening and Assembly | - Holes with a radius of 1.6 mm shown as empty in the CAD model shall be riveted using suitable rivets compatible with the material and thickness of the joined parts. - Holes with radii of 2.05, 2.1, 2.25, and 2.5 mm shown in the CAD shall be assembled using M4 screws, as indicated in the CAD model. - Where threaded fastening is required in sheet metal parts, suitable self-clinching nuts and lock nuts shall be used, selected according to the local assembly and accessibility requirements. - Alignment (locating) pins (Part no: 15) shall be provided on the connector plate (Part no: 42) as shown in the CAD model. The pins shall ensure repeatable positioning and prevent misalignment of mating components during assembly. - Unless otherwise specified, all holes intended for mechanical assembly shall be fastened using suitable fasteners (e.g. screws, bolts, rivets, or equivalent), selected according to hole size, material, and structural function. - Fasteners shall ensure secure assembly, proper engagement of mating components, and compatibility with the materials used. Where required, suitable locking methods shall be applied to prevent loosening under service conditions. - All components shall be assembled without excessive force. - Threads shall be fully engaged and free from damage. See Annex A, § 9. Annexes. |
| Material / corrosion compatibility | - Materials and fasteners shall be compatible to avoid galvanic corrosion. |
| Edge quality / Deburring | - All edges shall be free from burrs and sharp edges. Edges shall be deburred to ensure safe handling and proper assembly. - Holes shall be free from burrs and suitable for fastening. |
| Flatness / Deformation | According to ISO 2769-mK. Additionally, support surfaces shall be sufficiently flat to ensure proper seating of mating components. |
| Surface condition | Surface condition shall not impair assembly or function of mating components. |
| Manufacturing | The supplier is free to choose the manufacturing process, provided that all specified dimensions and requirements are met. |
| Quality/Inspection | - The supplier shall ensure that all dimensions comply with the specified tolerances and that all requirements are met. - The supplier shall verify that the Chassis allows correct integration of all subcomponents without interference or assembly issues, using the full assembly model provided in Annex C. Subcomponents are not part of the supply. See Annex C, § 9. Annexes. - Inspection records shall be provided upon request. |
| Delivery condition | The chassis shall be delivered fully assembled, free from damage, burrs and contaminants, and suitably protected for transport. |

## Operational and Environmental Conditions

The Supply will be located indoors and shall be capable of sustaining the following ambient conditions without degrading the performance ratings stated in this Technical Specification:

- At an altitude of approximately 400 meters above sea level;

- In ambient air temperature that varies between –5°C and + 50 °C;

- In relative humidity of at least 50% at + 50°C, non-condensing.

# SPECIFICATION OF THE ACTIVITIES

The Supply shall include the activities listed in the present section. These activities shall comply with the requirements specified below.

## Activities at the Contractor’s Premises

During the Contract, CERN shall have free access, upon request and during normal working hours, to the Contractor’s premises, including manufacturing and assembly sites and Subcontractor’s premises. The change of manufacturing place is subject to prior written approval by CERN.

### Prototype Manufacturing

The Contractor shall produce one prototype unit of the Ventilation Chassis for 19’’ Racks, according to the requirements specified in § 3.

Manufacturing of the series units will be subject to prior written acceptance of the prototype by CERN (see § 7.3).

CERN reserves the right not to order the prototype.

### Pre-series and Series Manufacturing

The Contractor shall produce 49 series units of Ventilation Chassis for 19’’ Racks, according to the requirements specified in § 3.

In case of differences between the series and the prototype units, CERN may request the Contractor to modify the series units concerned in order to remedy such differences.

### Packing and Shipping Conditions

The Contractor shall be responsible for the packing and the transport to CERN. In this case, the Contractor shall take up a dedicated all-risk transport insurance for the Supply concerned in accordance with the provisions of DAP Incoterms 2020 conditions, CERN Meyrin (CH).

In all cases, the Contractor shall comply with the packing and shipping instructions available under: https://procurement.web.cern.ch/system/files/document/packing-and-shipping-instructions_0.pdf and, in particular, ensure that the Supply is packed in a way that guarantees the absence of any contamination and that no damage or any possible deterioration in performance due to transport conditions can occur.

# SPECIFICATION OF THE DOCUMENTATION

The Supply shall include the documentation related to the Supply (§ 5.1). This documentation shall comply with the requirements specified below.

## Documentation Related to the Supply

The documentation related to the Supply shall include:

- Material certificate in accordance with EN 10204 (minimum type 2.2).

# APPLICABLE RULES, NORMS AND STANDARDS

The Supply shall comply with Laws. For the purpose of the Contract, Laws shall include all relevant rules, norms, and standards and, in particular those in § 3.1.

The supply shall comply in all respects with CERN Safety Instructions and the relevant IEC standards, recommendations and reports including their latest revisions. All CERN Safety Instructions can be obtained from the website: Safety rules | HSE unit at CERN

## Norms and Standards

The Supply shall be compliant with the following standards:

Table 2: Standards

| DIN EN ISO 2768:2025 | Geometrical product specifications (GPS) - Dimensional tolerancing - Tolerance limits for general specification of linear and angular sizes (ISO/DIS 2768:2025) |
| --- | --- |
| IEC 60297-3-106:2010 ED1 | Mechanical structures for electronic equipment - Dimensions of mechanical structures of the 482,6 mm (19 in) series - Part 3-106: Adaptation dimensions for subracks and chassis applicable with metric cabinets or racks in accordance with IEC 60917-2-1 |
| EN 10204 | Metallic products - Types of inspection documents |
| IEC 60917-1 | Modular order for the development of mechanical structures for electronic equipment practices – Part 1: Generic standard. |

# PERFORMANCE OF THE CONTRACT

## Schedule

The Contractor shall deliver the Supply in accordance with the following schedule, starting from the date of notification of the Contract to the Contractor:

Table 3: Schedule

|  | Milestones | Weeks | Indicative Date |
| --- | --- | --- | --- |
| T0 | Notification of the Contract to the Contractor. | T0 | June 2026 |
|  |  | T0 + 4 weeks |  |
| T1 | Delivery of the prototype unit at CERN and associated documentation. | T1 | July 2026 |
| T2 | Acceptance by CERN of the prototype and authorisation to proceed with the series production. |  | July 2026 |
|  | Delivery of series units at CERN and related technical documentation. | T2 + 12 weeks | October 2027 |

## Contract Follow-Up and Progress Monitoring

The Contractor shall assign a person in charge of the technical execution of the Contract and its follow-up, as well as a person in charge of the commercial follow-up, during the whole duration of the Contract. These persons shall be able to communicate (spoken and written) in at least one of the official languages of CERN (English or French).

## Acceptance of the Supply by CERN

### Acceptance of the Prototype

The Contractor shall deliver the prototype to CERN for acceptance, according to the schedule defined in § 7.1.

CERN will verify the conformity of the prototype in accordance with clause 22 of the General Conditions of CERN Contracts.

The ordering of components and the start of the production of the series units shall be subject to CERN’s prior written approval of the prototype units.

### Acceptance of the Series Units

The Contractor shall deliver to CERN for acceptance the series units as specified in

§ 4.1.3 and according to the schedule defined in § 7.1.

CERN will verify the conformity of the series in accordance with clause 22 of the General Conditions of CERN Contracts.

# CERN REPRESENTATIVES

All commercial and technical correspondence concerning the Price Enquiry shall be communicated to the CERN Procurement officer and in copy to the Technical officer. Any communication by or to any other person than the CERN Procurement Service shall not be valid and have no effect.

Table 4: Procurement & Technical Officers

| Procurement officer | Tel | Email |
| --- | --- | --- |
| XXX |  |  |
| In case of absence: |  |  |
| Technical officer | Tel | Email |
| Sedef Zeynep Bas | ### +41227665016 | sedef.zeynep.bas@cern.ch |
| In case of absence: |  |  |
| Gerardo Velazquez Gutierrez | ### +41227667851 | gerardo.velazquez.gutierrez@cern.ch |

# ANNEXES

The technical documentation supporting this specification is provided in the following annexes. These include the 3D CAD model of the ventilation chassis and the 2D drawings defining the critical dimensions.

In addition, a 3D CAD model of the fully assembled chassis with tangential fans is provided for reference purposes to illustrate the integration of the chassis with its subcomponents; however, this assembly and its components are not within the scope of this specification.

Table 5: Annexes

| Annex A | .step file of the CAD model of the Ventilation Chassis for 19’’ Racks |
| --- | --- |
| Annex B | 2D Drawings of the critical dimensions |
| Annex C | .step file of the fully assembled chassis with tangential fans - for information purposes |